| Topic | Undesirable Example | Proper Example |
| --- | --- | --- |
| HOSES AND CONNECTIONS Connections must be made with approved fittings. Tape not permitted. Hoses must be replaced if it fails a leak test, shows visible damage or soiled. Leak check system components at least monthly. Date system with last leak check. |  |  |

| Topic | Undesirable Example | Proper Example |
| --- | --- | --- |
| NOSE CONES Use commercial nose cones. Membrane required for non- angled nose cones. Membrane must enclose both nose and mouth. Replace membrane when slit is too large or if cracking is observed. |  |  |
| Topic | Undesirable Example | Proper Example |
| STEREOTAXIC FRAME-RODENT Waste anesthetic gas must be scavenged. |  |  |

| Topic | Undesirable Example |  | Proper Example |
| --- | --- | --- | --- |
| INDUCTION CHAMBERS Household plasticware not permitted. Induction chamber must vent into a ducted BSC, fume hood, or charcoal filter. If not housed in a ducted BSC, or fume hood, flush chamber with air before opening. |  |  |  |
| CHARCOAL CANISTER Must be supported such that discharge openings are not occluded. Canisters should be weighed after each use. Replace F/Air canister when it reaches 50g. Follow manufacturer’s recommendations. Dispose through chemical waste stream |  |  |  |
| Topic |  | Undesirable Example | Proper Example |
| VAPORIZERS Calibrate - (1-2 years) Filled in fume hood or use a keyed refill tool. Vaporizers must be secured by frame or equivalent. Vaporizers are anesthetic specific |  |  |  |
| GENERAL CONDITIONS Anesthesia may not be used in areas with recirculating ventilation systems or areas with less than 4 ACH |  |  |  |

NOTES